## Slide 1: Heat Pump Exercise Sessions
Thermal Systems: Basic Aspects (H9X52A)
Toegepaste Thermodynamica (I0P29A)

## Slide 2: What is a heat pump?

## Slide 3: Schematic of heat pump
The heat pump takes heat from a source and pumps it to a sink
Consequently the temperature at the sink is higher than the temperature at the source
  TH > TL
Is this normal?
    NO – heat flows naturally from hot to cold, not the other way around (i.e. the heat pump case)
So what is missing?
    An input of energy is needed in order to make this unnatural process happen
HEAT PUMP
SINK
SOURCE
QH
QL
QH = heat high QL = heat low
Notes: The main goal of a heat pump is to use heat from a source at low temperature to deliver heat at high temperature at the sink side of the heat pump

## Slide 4: What are the components of a heat pump?
Evaporator
Condenser
Expander
Compressor

## Slide 5: Heat Pump: the details
There are 3 circuits having three different compounds flowing through them (ṁ = mass flow):
  ṁref (1 to 4) = refrigerant
    Freon, butane, propane….
    Steps 1-2 VAPOUR  crucial for functional compressor
    Steps 3 LIQUID
    Step 4 LIQUID + VAPOUR
  ṁWC (5 to 6) = water
    Water which goes to our radiators
  ṁWE (7 to 8) = water + alcohol
    We add an alcohol ( e.g. ethanol) to lower the freezing point - ensure smooth functioning of evaporator
Ẇ
Evaporator
Condenser
Compressor
QH
QL
Expander
1
2
3
4
5
6
7
8
ṁWC
ṁWE
ṁref
Notes: The refrigerant evaporates at low pressure and at a temperature lower than the source temperature level – extracts the heat at low temperature
The refrigerant is then compressed – gas condenses at high pressure and at a temperature higher than the sink – delivering heat

## Slide 6
QH
QL
W

## Slide 7
QH
QL
W

## Slide 8: Pressure-enthalpy diagrams
Processes:
  1-2  compression  isentropic
  2-3  condensing  isobaric
  3-4  expansion  isenthalpic
  4-1  evaporating  isobaric
QH
QL
W

## Slide 9: How do we measure the performance of a HP?
Electric power of compressor (Ẇ)
Heat power delivered by condenser (QH or QC)

## Slide 10: Coefficient of performance (COP)
The performance of a heat pump is formally known as the COP:
The maximum theoretical performance is defined by Carnot’s equation:

## Slide 11: So how can we obtain Ẇ and QC?
ENTHALPY (H)
Energy content of a substance
QH
QL
W

## Slide 12: Obtaining Ẇ and QC
Ẇ
Evaporator
Condenser
Compressor
QH
QL
Expander
1
2
3
4
5
6
7
8
ṁWC
ṁWE
ṁref
Two ways of calculating QC
1. Using refrigerant mass flow
2. Using condenser water mass flow
Can use the specific heat capacity of water (Cp) - H2O is a non-compressible liquid

## Slide 13: Calculating COP: two possibilities
Using refrigerant information
Using water information (when HP is a black box)

## Slide 14: Sankey diagram
A flow diagram  width of arrow is proportional to flow quantity
Show the energy flows between the HP components using a Sankey diagram
Consider what is going in/out of each component of the HP as well as losses
Will be a cycle
LED light example
Condenser
Compressor
Expander
Evaporator
http://www.myphysics.org.uk/ks4p3hotpot04.htm

## Slide 15: E.g. Sankey for compressor
Law of conservation of energy – total energy of an isolated system is constant, energy can be transformed from one form to another but it cannot be created or destroyed.
Compressor

## Slide 16: Your turn!
Download all matlab files from Toledo (Calculations_template)
Instructions and questions  2 weeks
*Used to be able to access a heat pump
Change input parameter, observe new steady state, defined by outputs:
  4 pressures, 8 temperatures, 3 flows, W
5 settings = cols, in each setting find the outputs
Input all data  perform calculations
First theory part requires no data

## Slide 18: Temperature behavior
http://www.heatpump-reviews.com/pressure-enthalpy-chart.html

## Slide 19
https://www.sciencedirect.com/science/article/pii/B9780081003114000017
QH
QL
W